## Factory Configuration
CCN Point Name | Value | Description
unitsize | 140 | Unit Capacity
voltage | 460 | Power Supply Voltage
freq_60H | 1 | 60Hz Sel (No=50, Yes=60)
mfg_tier | 0 | Tier 0=STD, 1=MID, 2=HI
probrine | 0 | Process Brine Evap
cpass_nb | 2 | Evap Pass Number
heat_sel | 0 | Evap Heater Installed
mst_slv | 1 | Master Slave Setup
emm_nrcp | 1 | Energy Management Module
loambopt | 0 | Low Ambient Option (STD)
leak_chk | 0 | Leakage Charge Detection
fMaxEnA | 0 | Enable Max Frequency A
fMaxEnB | 0 | Enable Max Frequency B
fMaxOvrA | 75 | Max Frequency Override A
fMaxOvrB | 75 | Max Frequency Override B
fan_fact | 1 | Fan Freq Factor(0.7-1.1)
fMinOvr | 26 | Min Frequency Override
lastspda | 40 | Low Amb. Start Spd A
lastspdb | 40 | Low Amb. Start Spd B
ECM_fans | 0 | ECM fans sel. swtch
PM_Motor | 1 | PM motor sel. swtch
CondCoil | 0 | Cond Coil type option

## Service Configuration
CCN Point Name | Value | Description
flui_typ | 1 | Evaporator Fluid Type
ewt_opt | 0 | Entering Fluid Control
freezesp | 34 | Brine Freeze Setpoint
mini_lwt | 38 | Brine Minimum Fluid Temp
fastcapr | 0 | Fast Capacity Recovery
ewt_cirA | 1 | EWT Probe on Cir A Side
leak_thr | 2.5 | Leakage Charge Threshold
leak_tmr | 60 | Leakage Charge Timer
ecodgt | 0 | Enable Eco Exv Dgt Prot.
RFI_conf | 1 | Compressor RFI Filter En
metric | 0 | Metric Units? (Blackbox)
fdrv_cfg | 1 | Send fan drive config?
cdrv_cfg | 1 | Send comp. drive config?
heatersp | 2 | Evap Heater Delta Spt
freez_ov | 0 | Freeze Override Offset
auto_sm | 0 | Auto Start When SM Lost
ViPwrChk | 1.15 | VI Self-Test Threshold
ViChkEn | 0 | VI Self-Test Enable
AntiFrz | 1 | Pump Rot. AntiFrz Protec
odtrspd | 5 | Oil Delta Trigger Speed
otrigtim | 3600 | Oil Trigger Time
odrecspd | 5 | Oil Delta Recover Speed
orectim | 60 | Oil Recover Time
wateesys | 0.9 | Water Temp Hysteresis
vistrtdt | 900 | High VI Time at Start
vistrten | 1 | Enable High VI at Start
apr_en | 1 | Approach Ctrl at Start?
cmpapr | 30 | C. Prot. APR Limit
cmpsst | 20 | C. Prot. SST Frz Offset
cmpdsst | -18 | C. Prot SST dT Limit
cmpdgt | 185 | C. Prot. DGT Limit
cmpddgt | 13.5 | C. Prot. DGT dT Limit
cmptmr | 60 | C. Prot. Start Time
SnsrSwp | 0 | Sensor_Swap_Alarm